# SGH RAAC Project – Internal Action Plan

# Version Control / Change Record

| Date | Author | Version | Page | Reason for Change |
| --- | --- | --- | --- | --- |
| May 2022 | [redacted] | 1.0 |  | New |
| June 2022 | Review [redacted] | 1.1 | 1 | 1.2 update, 3.1 update, 2.1 update |

Version Page Reason for Change

# Action Log

| Action | Description | Deadline | Owner | Notes / Progress (Completed / Open) |
| --- | --- | --- | --- | --- |
| 1 | Documentation |  |  |  |
| 1.1 | Plan of RAAC affected areas showing departments underneath it | In place | [redacted] | Photograph produced showing all affected areas. |
| 1.2 | Need to add risk assessment and reporting via Board Assurance Framework if appropriate | June 22 v1.1 | [redacted] | RA reviewed and updated June 22 |
| 1.3 | Plan showing the location of every RAAC plank with unique identifier – to support surveying and ultimately to record plank condition | 30/04/2022 | [redacted] | Appointment of Curtins required? |
| 1.4 | Photographs and drawings of Buildings and RAAC Planks in-situ to enable SCOSS to create a database of all instances of RAAC | Ongoing | [redacted] | Appointment of Curtins required? |
| 2 | Surveying |  |  |  |
| 2.1 | Visual inspection of every plank to determine: - Deflection - Spalling - Cracking - Water Ingress - non-standard planks | 30/04/2022 | [redacted] | Standard Planks, flat planks on flat areas (?) Appointment of Curtins required? Estates twice weekly visual inspection in place for affected areas |
| 2.2 | Establishing the end bearing of the plank and the transverse reinforcement position in relation to it through: - Assessment of historic construction details, - Assessment of as built construction - Plank manufacturing quality (consistency) - Cover Meter assessment of planks - Method of investigation for roof coverings that prevent use of cover meter (foil backed insulation) - Identification of plant on roof and mitigating actions to spread/mitigate load | 30/06/2022 | [redacted] | Appointment of Curtins required? Type 3 survey? |
| 2.3 | To undertake an annual survey of every plank; or more frequently as advised by appointed structural engineer | 30/04/2023 | [redacted] |  |
| 3 | Communication |  |  |  |
| 3.1 | Inform Executive and Board of the current position on RAAC Plans and the Risks Regular progress reports to Board and Board sub committees (+ ICS) Legal advice to Boards regarding timing/ rational for decisions made | Annual survey / ongoing | [redacted] | AB updated Exec 20 June 22 |
| 3.2 | Inform Staff of the presence of RAAC Planks, the issues, and actions to take in the event of: Deflection; Spalling; Cracking; Water Ingress; Dust/Debris; and/or Noises within the structure (Posters in staff only facing areas may be considered as part of an internal staff engagement and communication plan) | Ongoing | [redacted] | Be part of a communications approach led by NHS England and NHS Improvement, cognisant of: SCOSS Guidance; Duty of Candour; and duties under the Health and Safety at Work (etc) Act 1974 |
| 4 | Action Cards |  |  |  |
| 4.1 | Adopt the West Suffolk Action Cards in respect of: - Permits to Work - Weather – Snow - Weather – Wind - Weather – Rain - Deflection - Spalling - Cracking - Water Ingress - Dust - Debris - Noises - Acrow Propping - Training and support to estate teams for the above | Immediate | [redacted] | Within 2 weeks of RAAC discovery, or as soon as reasonably practicable |
| 5 | Emergency Planning Preparedness |  |  |  |
| 5.1 | To have undertaken a desktop evacuation plan within the last 12 months; and every subsequent 12 months |  | [redacted] |  |
| 6 | Operational Measures |  |  |  |
| 6.1 | To identify remedial actions and works to minimise risks | 30/06/2022 | [redacted] |  |
| 6.2 | Remedial works repairs | Immediately when issues are identified | [redacted] |  |
| 6.3 | Worked up plans ready for implementation to minimise shear risk | 30/06/2022 | [redacted] |  |
| 7 | Strategic / Capital Planning |  |  |  |
| 7.1 | Relocation of Pathology staff (FF) | 30/06/2022 | [redacted] |  |
| 7.2 | Assessment of Pathology block demolition costs and timeline | 30/06/2022 | [redacted] |  |
| 7.3 | Assessment of decanting requirements for Pathology at SGH, costs and timeline | 30/06/2022 | [redacted] |  |
| 7.4 | Assessment of replacement building for Pathology at SGH (scope, cost, timeline) | 30/06/2022 | [redacted] | Cost estimate received but further work required on scope and timeline. |
| 7.5 | Assessment of work required to eradicate RAAC from main link corridor | 30/06/2022 | [redacted] | IHP instructed to provide a proposal for the elimination / management of RAAC in this location (using Curtins). |
| 7.6 | Assessment of work required to eradicate RAAC from Pathology link corridor | 30/06/2022 | TBC |  |
| 7.7 | Assessment of work required to eradicate RAAC from Theatre block roof area | 30/06/2022 | TBC |  |
| 8 | Reporting |  |  |  |
| 8.1 | Quarterly reporting incidences of Deflection, Spalling and Cracking to NHSE and NHSI Attendance at RAAC support group | 04/2022 07/2022 10/2022 | [redacted] |  |
| 8.2 | Quarterly reporting of progress against this action plan to NHSE and NHSI | 04/2022 07/2022 10/2022 | [redacted] |  |

KEY

| Abbreviation | Definition |
| --- | --- |
| [redacted] | [redacted] (LLP Estates) |
| [redacted] | Paul Johnson (LLP Estates) |
| [redacted] | [redacted] (Trust Head of Safety and Security) |
| [redacted] | [redacted] |
| [redacted] | [redacted] (LLP Head of Capital Projects) |
| [redacted] | Integrated Health Projects (P22 Principal Supply Chain Partner) |